iSMA-B-LP / iSMA-B-LP-1

|  | iSMA-B-LP is a wall panel with 2.3” LCD display and four function buttons. Additionally, the panel has the built-in temperature sensor and optionally the humidity and CO2 sensors. iSMA-B-LP is powered with 24 V AC/DC and has the built-in RS485 port (Modbus RTU/ASCII, BACnet MSTP). Use of open communication protocol allows to connect the panel with any controller supporting Modbus RTU/ASCII or BACnet MSTP. Together with iSMA-B-FCU controller, the panel allows to change the basic parameters such as: temperature setpoint, fan speed, FCU mode and others. Thanks to built-in USB port, there is possibility to maintenance the panel configuration without the power supply. iSMA-B-LP has the modern design and it is available in different colours at client’s request, and also in two versions of button icons appearance. | # Key Features - 2.3” LCD display with backlight - 4x function buttons - Built-in temperature, CO2 and humidity sensors - Modbus RTU/ASCII - BACnet MSTP - Wall mounting (standard electric box – 60 mm/2.3622 in) - Changing of the basic parameters in conjunction with FCU controller - 2x RJ12 for fast connection to FCU controller - 7 main menu categories - Over 100 freely configurable variables - Possibility to display the current time |  |
| --- | --- | --- | --- |

iSMA-B-LP-1

iSMA-B-LP

| Temperature sensor: - Type: 10k NTC - Range: 0 – 50°C (32°F – 122°F) - Accuracy: +/- 0,5°C (0,9°F) - Resolution: +/- 0,1°C (0,18°F) Humidity sensor: - Range: 0-100% RH - Accuracy: +/- 2% RH in range 20 – 80% RH - Resolution: +/- 1% RH CO2 sensor: - Method Non Dispersive Infrared (NDIR), gold plated optics, diffusion sampling (with Telaire’s Patented ABC Logic Self Calibrated Algorithm) - Range: 400 – 2000 ppm - Accuracy: +/- 30 ppm OR +/- 3% of reading - Stability: < 2% of FS over life of sensor (15 years typical) - Warm Up Time : < 2 minutes (operational); 10 minutes (maximum accuracy) - Calibration: ABC Logic Algorithm - Manual Calibration Interval: Not required |  | Communication - 2x RJ12 terminal (RS485 half-duplex) - Baud rate: 2400 to 115200 bps - Protocols: Modbus, BACnet - MINI USB, Type B Platform - ARM Cortex: M0+ Housing - Dimension: 100x123x27 mm (3.9371x4.8426x1.063 in) - Construction: plastic, self-extinguishing (PC/ABS) - Wall mounting (standard electric box) - Cooling: internal air circulation Environment - Operating temperature: 0°C to 50°C (32°F to 122°F) - Storage temperature: -40°C to 85°C (-40°F to 185°F) - Relative humidity: 5% to 95%, no condensation - Ingress Protection Rating: IP20 - For indoor installation Power supply - 24 V AC/DC +/- 20% |  |
| --- | --- | --- | --- |
| Type | Temperature | Humidity | CO2 |
| iSMA-B-LP(-1) | √ |  |  |
| iSMA-B-LP-H(-1) | √ | √ |  |
| iSMA-B-LP-C(-1) | √ |  | √ |
| iSMA-B-LP-HC(-1) | √ | √ | √ |